## introduction
ISO/NP 13675
Heating systems in buildings — Method for calculation of system energy requirements and system efficiencies — Modul 3 - 8 — Part 4-1: Space heating generation systems, combustion systems (boilers) oil, gas, coal, biomass
In this exel-document is written the calculation of the draft prEN 15316-4-1 dated 19.09.2013
The following colours have the described senses
|  | input of data for intended calculation | you have to input data and choos parameters
adoption, not calculated
fixing of equippment and parameters
|  | transfered datas from other pages or tables | for information
calculation
result for output

## In-output
5.2 Input quantities from other parts of the heating system standards
Table 3 - Input quantities
Notation | Meaning | Reference | Input | unit
Etgen;del;in | Delivered energy input of the generation sub-system (measured fuel input) (in the calculation interval), in kg, m³,l | see |  | kWh/intervall
Pn | generator output at full load, in kW | see | 70 | KW
tH | heating hours (in the calculation interval), in s/h or h/mth | see ISO 13790 | 720 | h/intervall
tXY | operating hours for other services(in the calculation interval), in s/h or h/mth | see | 0 | h/intervall
QH;dis;in | heat input to the heating distribution | see | 105000 | kWh/intervall
QXY;dis;in | heat input to the other services distribution | see | 10500 | kWh/intervall
bXY;gen | actual load factor for other services, in - | see | 0 | -
bH;gen | actual load factor for heating system, in - | see | 0.6 | -
Je | external air temperature, in °C | see external climat data |  | °C
Je;min | daily average design temperature, in °C; | see external climat data |  | °C
JHc;mn | generator average water temperature (or return temperature to the generator for condensing boilers) as a function of the specific operating conditions for heating | see | 48.9 | °C
JXYc;mn | generator average water temperature (or return temperature to the generator for condensing boilers) as a function of the specific operating conditions for other services
JHc;RT | return temperature to the generator for condensing boilers as a function of the specific operating conditions for heating | see | 37.7 | °C
JXYc;RT | return temperature to the generator for condensing boilers as a function of the specific operating conditions for other services
Jbrm | ambient temperature, in °C | see |  | °C
to decide
| calculation way: starting with measured values or by designing: | designed
| heat load definition, if designed | heat load calculation
flue gas measurement |  |  | Input | unit
XO2;fg;dry | flue gas oxygen contents |  | 1.1 | Vol-%
Egen;del;in | Delivered energy input of the generation sub-system (measured fuel input) (in the calculation interval), in kg, m³,l |  | 8 | m³; kg; l
Jgen;meas | average water temperature in the boiler – or for condensing boiler return temperature corresponding to Jgen;ref = 60 °C - during measurement of fch;on;meas |  | 60 | °C
Jch | flue gas temperature |  | 35 | °C
Jbrm | installation room temperature |  | 25 | °C
envelope of the boiler, diameter and temperature |  | breadth | extent | Jexpanse
| (dimension) | m |  | °C
| front | 0.95 | 0.6 | 35
| back | 0.95 | 0.6 | 32
| left side | 0.95 | 0.77 | 29
| right side | 0.95 | 0.77 | 29
| top | 0.6 | 0.77 | 34
5.3 Output quantities for other parts of the heating system standards
Table 4 - Output quantities
Notation | Description | Reference | Input | unit | note
Egen;in | Fuel heat requirement | see 7.5 | 115384.3948 | m³/intervall | see calculation 4.
Qgen;ls;rbl | generation heat losses for the heating system to the installation room space (in the month), in kWh | see 7.4.3.2 | 175.0623 | kWh/intervall | see calculation 5.2
Wgen | heat generation auxiliary energy for the heating system (in the month), in kWh | see 7.4.2 | 156.1403 | kWh/intervall | see calculation 5.2
| to decide | Inpu-/output calculation: | design mistake
choos parameters | Boiler type
Gas-Condensing boiler, improved - from1994
Boiler/contoler type
Floor standing boiler - Outdoor temperature controlled
Generator location
In the boiler room
Parameters for measurement, if intended
| fuel | for measurment calculation there are some parameters not available at the moment, so the calculation does not work in these cases.
natural gas
Liquid fuel or gas fired boiler with the fan before the combustion chamber and automatic closure of air intake with burner off:

## measurment
[11 empty] | Indexchange: | bint = bPint
chapter | equation | flue gas measurement |  | Input | unit
6.1.1 |  | XO2;fg;dry | flue gas oxygen contents | 1.1 | Vol-%
|  | Egen;del;in | Delivered energy input of the generation sub-system (measured fuel input) (in the calculation interval), in kg, m³,l | 8 | m³; kg; l | [5 empty] | Annex A
|  | Jgen;meas |  | 60 | °C | [5 empty] | Additional formulas and default values for parametering the boiler efficiency method
|  | Jch | flue gas temperature | 35 | °C
|  | Jbrm | installation room temperature | 25 | °C | [5 empty] | A.4 Fuel constants for fluegas measurement depending on Siegert constants
[8 empty] | copy out of table A.9 |  |  | Table A.9 — Fuel constants for fluegas measurement depending on Siegert constants |  |  | Hs | Hi | Vair,st,dry | Vfg,st,dry | mH2O,st | (conversion factor for delivered energy) fHs/Hi
[8 empty] | natural gas |  |  |  | c10 | c11 | kJ/kg or kJ/Nm³ | kJ/kg or kJ/Nm³ | Nm³/kg or Nm³/Nm | Nm³/kg or Nm³/Nm | kg/kg or kg/Nm³
| 1 | fch;on;meas | fch;on;meas = (Jch - Jbrm) x (c10/(21% - XO2) + c11) | 0.42166 | - |  | c10 = | 0.66 |  |  | natural gas | 0.66 | 0.009 | 35169 | 31652 | 8.4 | 7.7 | 1.405 | 1.11
[7 empty] | c11 = | 0.009 |  |  | liquid gas (Propan) | 0.63 | 0.008 | 101804 | 93557 | 23.8 | 21.8 | 3.3 | 1.09
[11 empty] | fuel oil | 0.68 | 0.007 | 45336 | 42770 | 11.23 | 10.49 | 1.18 | 1.06
| 2 | fch;on | fch;on = fch;on;meas - (Jgen;ref - Jgen;meas) x fcorr;ch;on | 0.41266 | - |  | Jgen;ref | 80 | °C |  | Anthracite coal | [7 empty] | 1.04
[7 empty] | fcorr;ch;on | 0.045 | %/°C |  | Lignit coal |  |  | #REF! | 25122 |  |  |  | 1.07
[11 empty] | Wood |  |  | 15822 | 14650 | 3.8 | 4.5 | 0.7 | 1.08
[11 empty] | heavy oil | 0.68 | 0.007 |  | 39800
[11 empty] | city gas | 0.63 | 0.011
6.1.1.2 | 3 | fgen;env | fgen;env = S (Apa x a x D Jpa) / (1000 x Pgen;del) | 0.0028008 | - | [5 empty] | 5.2.1.2 Thermal losses through the generator envelope fgen;env
[12 empty] | breadth | extent | Apa | a | Jexpanse | Jbrm | DJpa | Apa x a x D Jpa
[11 empty] | (dimension) | m |  | m² | W/m² | °C |  | K | W
[11 empty] | front | 0.95 | 0.6 | 0.57 | 10 | 35 | 25 | 10 | 57
[11 empty] | back | 0.95 | 0.6 | 0.57 | 10 | 32 | 25 | 7 | 39.9
[11 empty] | left side | 0.95 | 0.77 | 0.7315 | 10 | 29 | 25 | 4 | 29.26
[11 empty] | right side | 0.95 | 0.77 | 0.7315 | 10 | 29 | 25 | 4 | 29.26
[11 empty] | top | 0.6 | 0.77 | 0.462 | 10 | 34 | 25 | 9 | 41.58
[19 empty] | 197 | W
A.5 Default values for calculation of thermal losses through the chimney with the burner off
6.1.1.3 |  | fch;off | Liquid fuel or gas fired boiler with the fan before the combustion chamber and automatic closure of air intake with burner off: | 0.2 |  |  | see Annex table A.10 |  |  |  | Table A.10 — Default value of fch,off
[12 empty] | Description | fch,off
%
[12 empty] | Liquid fuel or gas fired boiler with the fan before the combustion chamber and automatic closure of air intake with burner off: | 0.2
[12 empty] | Premixed burners | 0.2
[12 empty] | Wall mounted, gas fired boiler with fan and wall flue gas exhaust | 0.4
[11 empty] | Liquid fuel or gas fired boiler with the fan before the combustion chamber and no closure of air intake with burner off: | Chimney height ≤ 10 m | 1
[12 empty] | Chimney height > 10 m | 1.2
6.1.1.4 | 4 | Pgen;ls;ch;on | Pgen;ls;ch;on = 0,01 x fch;on x Pgen;del | 0.29025 | kW |  | (measured O2)
| 5 | Pgen;ls;ch;off | Pgen;ls;ch;off = 0,01 x fch;off x Pgen;del | 0.14068 | kW
| 6 | Pgen;ls;env | Pgen;ls;env = fgen;env x Pgen;del | 0.197 | kW
A.6 Additional default data and calculation for condensing boilers
| 7 | Pcond | Pcond = Qcond /Hs x Pgen;del | 7.5372 | kW |  | see condensation
Table A.12 — Default fuel data for condensation heat recovery calculation
[11 empty] | Property |  | Symbol | Unit | Fuel
[15 empty] | Natural gas | Propane | Butane | Light oil EL
(Groningen)
[11 empty] | Unit mass of fuel |  |  |  | 1 Nm³ | 1 Nm³ | 1 Nm³ | 1 kg
[8 empty] | Kopie aus der Tabelle A.12 |  | kJ/kg | Gross calorific value |  | Hs | kJ/kg or kJ/Nm³ | 35169 | 101804 | 131985 | 45336
| 8 | Pgen;del | Pgen;del = Egen;in x Hi / 3600 | 70.3378 | kW |  | Hi = | 31652 |  | or | Net calorific value |  | Hi | kJ/kg or kJ/Nm³ | 31652 | 93557 | 121603 | 42770
[10 empty] | kJ/Nm³ | Stoichiometric dry air |  | Vair,st,dry | Nm³/kg or Nm³/Nm | 8.4 | 23.8 | 30.94 | 11.23
6.1.1.5 | 10 | hgen;Pn | hgen;Pn = (Pgen;del - Pgen;ls;ch;on - Pgen;ls;env)/Pgen;del | 99.3073 | - | [5 empty] | Stoichiometric dry flue gas |  | Vfg,st,dry | Nm³/kg or Nm³/Nm | 7.7 | 21.8 | 28.44 | 10.49
[11 empty] | Stoichiometric water production |  | mH2O,st | kg/kg or kg/Nm³ | 1.405 | 3.3 | 4.03 | 1.18
| 11 | hgen;Pint | hgen;Pint = (Pgen;del x bPint - (bPint x (Pgen;ls;ch;on - Pcond + Pgen;ls;env) + (1-bPint) x (Pgen;ls;ch;off + Pgen;ls;env)/(Pgen;del x bPint) | 1.089 | - | bPn | 1
[6 empty] | bPint | 0.3
| 12 | fgen;ls;P0 | fgen;ls;P0 = fch;off + fgen;env | 0.2028 | -

## Condensation(measurement)
Annex A
chapter | equation | A.6 Additional default data and calculation for condensing boilers
|  |  | out of measurement: |  |  | note |  |  |  | A.6 Additional default data and calculation for condensing boilers
|  | Jfg | flue gas temperature | 35 | °C | see measurement
|  | Jbrm | installation room temperature | 25 | °C | see measurement |  |  |  | Table A.11 — Saturation humidity as a function of temperature
|  | XO2;fg;dry | flue gas oxygen contents | 1.1 | Vol-% | see measurement or table A.12 |  |  |  | Temperature | °C | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70
[8 empty] | copy out of table A.11 |  | (Jair or Jfg)
[7 empty] | mH2O;air;sat | 0.016987 | kg/Nm³dry | Saturation humidity | kg/Nm³dry | 0.00493 | 0.00986 | 0.01912 | 0.03521 | 0.06331 | 0.1112 | 0.1975 | 0.3596
A.6 | A.9 | Vfg;dry | Vfg;dry = Vfg;st;dry x 20,94 / (20,94-XO2;fg;dry) | 1.4829 | m³/m³ or m³/kg |  | mH2O;fg;sat | 0.04507 |  | mH2O;air;sat or mH2O;fg;sat
NOTE Saturation humidity is expressed as kg of water vapour per Nm³ of dry gas (either air or flue gas).
| A.10 | Vair;dry | Vair;dry = Vair;st;dry + Vfg;dry - Vfg;st;dry) | 7.7779 | m³/m³ or m³/kg
| A.11 | mH2O;air | mH2O;air = mH2O;air;sat x Vair;dry x xair/100 | 0.066062 | kg/kg or kg/Nm³
| A.12 | mH2O;fg | mH2O;fg = mH2O;air;sat x Vair;dry x xair/100 | 0.066834 | kg/kg or kg/Nm³ |  |  |  |  | Table A.12 — Default fuel data for condensation heat recovery calculation
[8 empty] | copy out of table A.12 |  | Property | Symbol | Unit | Fuel
| A.13 | mH2O;cond | mH2O;cond = mH2O;st + mH2O;air - mH2O;fg | 1.4042 | kg/kg or kg/Nm³ | 1.4042 | Hs | 31652 | kJ/kg or kJ/Nm³ |  |  |  | Natural gas | Propane | Butane | Light oil EL | Liquid petroleum gas | Anthracite coal | Lignit coal | Wood
[7 empty] | Hi | 8.4 | kJ/kg or kJ/Nm³ |  |  |  | (Groningen)
| A.15 | hcond;fg | hcond;fg = 694,61-Jfg x 0,6765 | 670.936 | Wh/kg |  | Vair;st;dry = | 7.7 | Nm³/kg or Nm³/Nm | Unit mass of fuel |  |  | 1 Nm³ | 1 Nm³ | 1 Nm³ | 1 kg | 1 Nm³ | 1 kg | 1 kg | 1 kg
[7 empty] | Vfg;st;dry = | 1.405 | Nm³/kg or Nm³/Nm | Gross calorific value | Hs | kJ/kg or kJ/Nm³ | 35169 | 101804 | 131985 | 45336
| A.16 | Qcond | Qcond = mH2O x hcond;fg | 942.1466 | Wh/kg or Wh/Nm³ |  | mH2O;st = | 1.405 | kg/kg or kg/Nm³ | Net calorific value | Hi | kJ/kg or kJ/Nm³ | 31652 | 93557 | 121603 | 42770
[10 empty] | Stoichiometric dry air | Vair;st;dry | Nm³/kg or Nm³/Nm | 8.4 | 23.8 | 30.94 | 11.23
| A.17 | Pcond | Pcond = 3,6 x Qcond/ Hs x Pgen;del | 7.5372 | kW |  |  |  |  | Stoichiometric dry flue gas | Vfg;st;dry | Nm³/kg or Nm³/Nm | 7.7 | 21.8 | 28.44 | 10.49
[10 empty] | Stoichiometric water production | mH2O;st | kg/kg or kg/Nm³ | 1.405 | 3.3 | 4.03 | 1.18
Table A.13 — Default values for the calculation of Qcond
[10 empty] | Description | Symbol | Unit | Case | Value
[10 empty] | Combustion air relative humidity | xair | % | All cases | 50
[10 empty] | Flue gas relative humidity | xfg | % | All cases | 100
[10 empty] | Flue gas oxygen contents at maximum combustion power | XO2;fg;dry | - | All cases | 6

## calculation 4.
chapter | equation |  |  | Input | unit |  |  |  | note
7.5 | 33 | Egen,in | Egen,in=Qgen,out-Qgen,aux,rvd+Qgen,ls-Qgen,ren | 115384.3948 | kWh/intervall | Qgen;ren = | 0 | kWh/mth
[6 empty] | Qgen;aux;rvd = | 115.6052 | kWh/interval | see calculation 5. |  | Annex B General part default values and information
[6 empty] | Qgen;ls = | 0 | kWh/mth | see calculation 5.
| 34 | Qgen;out | Qgen;out=fctr;ls x Si QH;dis;in,i + Sj QXY;dis;in,j | 115500 | kWh/intervall | fctr;ls = | 1 | - | see tabel B.1 or B.2 |  | Table B.1 — Default values for control factor fctr,ls in equation (2)
[6 empty] | QH;dis;in,i = | 105000 | kWh/mth | see input |  | Description |  | fctr,ls
[6 empty] | QXY;dis;in,j = | 10500 | kWh/mth | see input |  | All control types |  | 1
|  | Pn |  | 70 | kW | see input: heat load calculation
|  | Pint | Pint = 0.3 x Pn | 21 | kW
out of measurement
6.1.1.4 | 9 |  | Pn = hgen,Pn x Pgen;del | 69.8505 | kW
[6 empty] | bPn | 1
[6 empty] | bPint | 0.3 |  |  |  | Table B.2 — Sample default national table for control factor in equation (2)
7.1 | 13 | tH;op | tH;op = tH - tXY,op | 720 | h/intervall | [5 empty] | Boiler/contoler type | fctr,ls
|  | tXY;op | tXY;op = tXY x bXY;gen | 0 | h/intervall | [5 empty] | Floor standing boiler - Outdoor temperature controlled | 1
[11 empty] | Wall hanged boiler - Outdoor temperature controlled | 1.03
[11 empty] | Wall hanged boiler - Room temperature controlled | 1.06
|  |  | designd power Pn = | 70 | kW |  |  |  | heat load calculation | 70
[9 empty] | no heat load calculation - new building | 720
[9 empty] | no heat load calculation - existing building | 0

## calculation 5.2
chapter | equation |  |  | Input | unit | [8 empty] | note
7.4.1.1 | 14 | hgen;Pn;corr | hgen;Pn;corr = hgen;Pn + fcorr;Pn x (Jgen;test;Pn - JHC;mn) | 100.0651 | % | [5 empty] | hgen,Pn = | 95.8451 | %
[7 empty] | hgen,Pn = | hgen,Pint = | fgen,ls,P0 = | choosen Pn = | Pn = | 70 | kW | see calculation 4.
[6 empty] | designed | 95.8451 | 103.0018 | 0.0073117 | 70 | fcorr,Pn = | 0.2 | - | see tabel
| 15 | hgen;Pn;corr | hgen;Pn;corr = hgen;Pn;60-(hgen;Pn;60 - hgen;Pn;30)/(Jgen;test;Pn;60 - Jgen;test;Pn;30) x (Jgen,test,Pn;60 - JHC,RT) | [7 empty] | Jgen,test,Pn = | 70 | °C | see tabel
[11 empty] | JHC,m = | 48.9 | °C | see input
| 16 | Pgen;ls;Pn;corr | Pgen;ls;Pn;corr = (fHs/Hi - hgen;Pn;corr)/ hgen;Pn;corr x Pn | 7.6495 | kW |  | hgen,Pn = | hgen,Pint = | fgen,ls,P0 = | choosen Pn = | fHs/Hi = | 1.11 | - | copy out of table 8 | Table A.8 — Conversion factors, as a function of energy carriers
[6 empty] | measured | 99.3073 | 1.089 | 0.2028 | 69.8505
7.4.1.2 | 17 | hgen;Pint;corr | hgen;Pint;corr = hgen;Pint + fcorr;Pint x (Jgen;test;Pint - JHC;m) | 99.2218 | % | designed | 95.8451 | 103.0018 | 0.0073117 | 70 | hgen,Pint = | 103.0018 | % |  | Energy carrier |  | ratio of gross calorific value to net calorific value Hs/Hi
[11 empty] | Pint = | 0 | kW | see calculation 4. + input
[11 empty] | fcorr,Pint = | 0.2 | - | see tabel
[11 empty] | Jgen,test,Pint = | 30 | °C | see tabel |  |  | (conversion factor for delivered energy) fHs/Hi
| 18 | PH;gen,ls,Pint,corr | PH;gen,ls,Pint,corr = (fHs/Hi - hgen,Pint,corr)/ hgen,Pint,corr x Pint | 0.11871 | kW
7.4.1.3 | 19 | PH;gen;ls;P0;corr | PH;gen;ls;P0;corr = Pn / hgen;Pn x fgen;ls;P0 x fHs/Hi x ((JHC;m - Ji;brm) / DJgen;test;P0)1,26 | 0.39177 | kW | [5 empty] | fgen,ls,P0 = | 0.0073117 | - | see tabel | Fuels | Fuel oil | 1.06
[11 empty] | Ji,brm = | 13 | °C | see tabel |  | Natural gas | 1.11
[11 empty] | Jgen,test,P0 = | 70 | °C | see input |  | Liquid petroleum gas | 1.09
[16 empty] | Anthracite coal | 1.04
7.4.1.4 |  | 0<bH;gen<bPint | [13 empty] | Lignit coal | 1.07
| 20 | PH;gen;ls;Px | PH;gen;ls;Px = bH;gen/bPint x (PH;gen;ls;Pint;corr - PH;gen;ls;P0;corr)+PH;gen;ls;P0;corr | -1.394 | kW | [5 empty] | bH,gen = | 0.6 | - | see input |  | Wood | 1.08
[11 empty] | bPint = | 0.3 | - | see input | Area/district heating by CHPa | Fossil fuels | 1
|  | bPint<bH;gen<bPn | [8 empty] | bPn = | 1 | - | see input |  | Renewable fuels | 1
| 21 | PH;gen;ls;Px | PH;gen;ls;Px = (bH;gen-bPint ) / (bPn - bPint) x (PH;gen;ls;Pn;corr - PH;gen;ls;Pint;corr)+PH;nen;ls;Pint;corr | 3.3462 | kW | [9 empty] | Area/district heating by heating power plants | Fossil fuels | 1
[16 empty] | Renewable fuels | 1
|  |  | if bH;gen<bPint than (22), 'if bH;gen>bPint than (23) | [11 empty] | Electricity | Electrical power source mix
|  |  | PH;gen,ls,Px = | 3.3462 | kW | [9 empty] | a These values are typical for average area heating/district heating systems with a 70% contibution by CHP plants
| 22 | QH;gen;ls | QH;gen;ls = PH;gen;ls;PX x tH;op | 2409.241 | kWh/intervall | [5 empty] | tH,op = | 720 | h/intervall | see input
[11 empty] | tXY,op = | 0 | h/intervall | see input
7.4.1.5 | 23 | Qgen;ls | Qgen;ls = SiQH;gen;ls,i + SjQXY;gen;ls,j | 2429.241 | kWh/intervall | [5 empty] | QXY;gen;ls,j | 20 | kWh
7.4.2 |  | 0<bH;gen<bPint | [8 empty] | Paux,Pn=(c7+c8 x (Pn)n/1000
| 24 | PH;aux;Px | PH;aux;Px = bH;gen/bPint x (Paux;Pint - Paux;P0)+Paux;P0 | 0.21555 | kW
[11 empty] | Paux,Pn = | 0.34583 | kW
|  | bPint<bH;gen<bPn | [8 empty] | Paux,Pint = | 0.11528 | kW
| 25 | PH;aux;Px | PH;aux;Px = (bH;gen-bPint ) / (bPn - bPint) x (Paux;Pn - Paux;Pint)+Paux;Pint | 0.21408 | kW | [5 empty] | Paux,P0 = | 0.015 | kW
if bH;gen<bPint than (26), 'if bH;gen>bPint than (27)
|  |  | Paux,Px = | 0.21408 | kW
| 26 | WH;gen | WH;gen = PH;aux,PX x tH;op | 154.1403 | kWh/intervall
| 27 | Wgen | Wgen = SiWH;gen,i + SjWXY;gen,j | 156.1403 | kWh/intervall | [5 empty] | WXY;gen;ls,j | 2 | kWh
7.4.3.1 | 28 | Qgen;aux;rvd | Qgen;aux,;vd = Wgen x frvd;aux | 115.6052 | kWh/intervall | [5 empty] | frvd,aux = | 0.75 | - | see Annex A.1.5.1
[11 empty] | frbl,aux = | 0.25 | - | see Annex A.1.5.2
| 29 | Qgen;aux;rbl | Qgen;aux;rbl = Wgen x (1 - fbrm) x frbl;aux | 26.9745 | kWh/intervall | [5 empty] | fbrm = | 0.3 | - | see tabel
7.4.3.2 | 30 | Qgen;ls;env;rbl | Qgen;ls;env;rbl = Pgen;ls;P0;corr x ( 1 - fbrm ) x fenv x tH;op | 148.0878 | kWh/intervall | [5 empty] | fenv = | 0.75 | - | see tabel
1710

## tabels
|  | copy out of tabel A.1 + A.2 + A.5 + A.6 | [6 empty] | Pn |  |  |  | Pint |  |  |  | P0
|  | Boiler type | Factor c1 | Factor c2 | Factor c3 | Factor c4 | Factor c5 | Factor c6 | c7 | foodnote | c8 | n | c7 | foodnote | c8 | n | c7 | foodnote | c8 | n | Jgen,test,Pn | Jgen,test,Pint |  | Jgen,test,P0 | fcorr,Pn | fcorr,Pint | fenv
[9 empty] | W |  | W |  | W |  | W |  | W |  | W |  | °C | °C |  | °C
|  | Gas-Condensing boiler, improved - from1994 | 94 | 1 | 103 | 1 | 4 | -0.4 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 |  | 0 | 0 | 70 | 30 | -0.4 | 70 | 0.2 | 0.2 | 0.75
copy out of tabel A.7
|  | Generator location | Temperature reduction factor fbrm | Installation room temperature Ji,brm
|  |  | - | °C
|  | In the boiler room | 0.3 | 13
Annex A |  | Additional formulas and default values for parametering the boiler efficiency method
|  |  | Table A.1 — Parameters for calculation of generator efficiency and temperature limitation |  |  |  | Table A.2 — Parameters for calculation of stand-by heat losses |  | Table A.5 — Parameters for calculation of power consumption of auxiliary equipment | [11 empty] | Table A.1 |  |  | Table A.2 | Table A.3 | Table A.4 | Table A.6
[9 empty] | Pn |  |  |  | Pint |  |  |  | P0
|  | Boiler type | Factor c1 | Factor c2 | Factor c3 | Factor c4 | Factor c5 | Factor c6 | c7 |  | c8 | n | c7 |  | c8 | n | c7 |  | c8 | n | Jgen,test,Pn | Jgen,test,Pint |  | Jgen,test,P0 | fcorr,Pn | fcorr,Pint | fenv
[9 empty] | W |  | W |  | W |  | W |  | W |  | W |  | °C | °C |  | °C
| Standard boilers: | standard boiler: Multi-fuel boiler - before1978 | 77 | 2 | 70 | 3 | 12.5 | -0.28 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 20 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Multi-fuel boiler - 1978 - 1987 | 79 | 2 | 74 | 3 | 12.5 | -0.28 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 20 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: solid fuel boiler (fossil and biomass fuel) - before1978 | 78 | 2 | 72 | 3 | 12.5 | -0.28 | 40 | b | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: solid fuel boiler (fossil and biomass fuel) - 1978 - 1994 | 80 | 2 | 75 | 3 | 10.5 | -0.28 | 40 | b | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: solid fuel boiler (fossil and biomass fuel) - after 1994 | 81 | 2 | 77 | 3 | 8 | -0.28 | 40 | b | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler up to 250 kW - before1978 | 79.5 | 2 | 76 | 3 | 8 | -0.27 | 40 |  | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler up to 250 kW - 1978 - 1994 | 82.5 | 2 | 78 | 3 | 7 | -0.3 | 40 |  | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler up to 250 kW - after 1994 | 85 | 2 | 81.5 | 3 | 8.5 | -0.4 | 40 |  | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler more than 250 kW - before1978 | 79.5 | 2 | 76 | 3 | 8 | -0.27 | 80 |  | 0.7 | 1 | 40 |  | 0.2 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler more than 250 kW - 1978 - 1994 | 82.5 | 2 | 78 | 3 | 7 | -0.3 | 80 |  | 0.7 | 1 | 40 |  | 0.2 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: atmospheric gas boiler more than 250 kW - after 1994 | 85 | 2 | 81.5 | 3 | 8.5 | -0.4 | 80 |  | 0.7 | 1 | 40 |  | 0.2 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.5
|  | standard boiler: Fan-assisted boiler (fossil and biomass fuel)e - before1978 | 80 | 2 | 75 | 3 | 9 | -0.28 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Fan-assisted boiler (fossil and biomass fuel)e - 1978 - 1986 | 82 | 2 | 77.5 | 3 | 7.5 | -0.31 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Fan-assisted boiler (fossil and biomass fuel)e - 1978 - 1994 | 84 | 2 | 80 | 3 | 7.5 | -0.31 | 0 | b | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Fan-assisted boiler (fossil and biomass fuel)e - after 1994 | 85 | 2 | 81.5 | 3 | 8.5 | -0.4 | 0 | b | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: automaticaly-fed pellet central boiler e, system with buffer tank - after 1994 | 90.7 | 2 | 93.1 | 3 | 14 | -0.28 | 40 |  | 2 | 1 | 40 |  | 1.8 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: automaticaly-fed wood chips central boiler e, system with buffer tank - after 1994 | 91.6 | 2 | 94.6 | 3 | 14 | -0.28 | 60 |  | 2.6 | 1 | 70 |  | 2.2 | 1 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Burner replacement (only fan-assisted boilers) - before1978 | 82.5 | 2 | 78 | 3 | 9 | -0.28 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
|  | standard boiler: Burner replacement (only fan-assisted boilers) - 1978 - 1994 | 84 | 2 | 80 | 3 | 7.5 | -0.31 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 50 |  | 70 | 0 | 0.04 | 0.75
| Low temperature boilers: | low temperature boiler: atmospheric gas boiler up to 250 kW - 1978 - 1994 | 85.5 | 1.5 | 86 | 1.5 | 6 | -0.32 | 40 |  | 0.148 | 1 | 40 |  | 0.148 | 1 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.5
|  | low temperature boiler: atmospheric gas boiler up to 250 kW - after 1994 | 88.5 | 1.5 | 89 | 1.5 | 6.1 | -0.4 | 40 |  | 0.35 | 1 | 20 |  | 0.1 | 1 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.5
|  | low temperature boiler: atmospheric gas boiler more than 250 kW - 1978 - 1994 | 85.5 | 1.5 | 86 | 1.5 | 6 | -0.32 | 40 |  | 0.148 | 1 | 40 |  | 0.148 | 1 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.5
|  | low temperature boiler: atmospheric gas boiler more than 250 kW - after 1994 | 88.5 | 1.5 | 89 | 1.5 | 6.1 | -0.4 | 80 |  | 0.7 | 1 | 40 |  | 0.2 | 1 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.5
|  | low temperature boiler: Circulation water heater (11 kW 18 kW and 24 kW) - before1978 | 84 | 1.5 | 82 | 1.5 | 2.2 | 0 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Circulation water heater (11 kW 18 kW and 24 kW) - 1978 - 1994 | 86 | 1.5 | 82 | 1.5 | 2.2 | 0 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Combination boilers KSpd - after 1994 | 86 | 1.5 | 82 | 1.5 | 2.2 | 0 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Combination boilers DLc - after 1994 | 86 | 1.5 | 82 | 1.5 | 1.2 | 0 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Fan-assisted boiler (fossil fuel)e - before1978 | 84 | 1.5 | 82 | 1.5 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Fan-assisted boiler (fossil fuel)e - 1978 - 1994 | 86 | 1.5 | 86 | 1.5 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Fan-assisted boiler (fossil fuel)e - after 1994 | 88.5 | 1.5 | 89 | 1.5 | 4.25 | -0.4 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Burner replacement (only fan-assisted boilers) - before1978 | 86 | 1.5 | 85 | 1.5 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
|  | low temperature boiler: Burner replacement (only fan-assisted boilers) - 1978 - 1994 | 86 | 1.5 | 86 | 1.5 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 40 |  | 70 | 0.04 | 0.04 | 0.75
| Condensing boiler (oil/gas)a | Condensing boiler - before 1987 | 89 | 1 | 95 | 1 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 30 | b | 70 | 0.2 | 0.2 | 0.75
|  | Condensing boiler - 1978 - 1994 | 91 | 1 | 97.5 | 1 | 7 | -0.37 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 30 | b | 70 | 0.2 | 0.2 | 0.75
|  | Condensing boiler - after 1994 | 92 | 1 | 98 | 1 | 4 | -0.4 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 30 | b | 70 | 0.2 | 0.2 | 0.75
|  | Gas-Condensing boiler, improved - from1994 | 94 | 1 | 103 | 1 | 4 | -0.4 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 30 | b | 70 | 0.2 | 0.2 | 0.75
|  | Oil-Condensing boiler, improved - from 1994 | 94 | 1 | 103 | 1 | 4 | -0.4 | 0 |  | 45 | 0.48 | 0 |  | 15 | 0.48 | 15 | f | 0 | 0 | 70 | 30 | b | 70 | 0.04 | 0.1 | 0.75
a If standard values for "condensing boilers improved" are used for the calculation, the product value for the boiler installed must exhibit the above given efficiency.
b For condensing boilers according to directive 92/42/EEC testing applies at a return path temperature of 30°C.
c DL: Boiler with integrated domestic water heating working on the instantaneous principle with heat exchanger (V < 2 l).
d KSp: Boiler with integrated domestic water heating working on the istantaneous principle with small storage tank (2 < V < 10 l).
e If there is a forced draught ventilator assisting the burner than the values Paux,Pn; Paux,Pint increase by 40 %.
f If a elctronic controller is used, otherwise Paux,P0 = 0.
Table A.2 — Parameters for calculation of boiler efficiency and temperature limitation
based on EN 303-5
|  | Boiler type | c1 | c2 | c3 | c4 | DJgen,test,Pn
°C
|  | Class 1 | 47 | 6 | 48 | 6 | 70
|  | Class 2 | 57 | 6 | 58 | 6 | 70
|  | Class 3 | 67 | 6 | 68 | 6 | 70
Table A.7 — Temperature reduction factor and default installation room temperature
|  | Generator location | Temperature reduction factor fbrm | Installation room temperature Ji,brm
|  |  | - | °C
|  | Outdoors | 1 | 4
|  | In the boiler room | 0.3 | 13
|  | Under roof | 0.2 | 5
|  | Inside heated space | 0 | 20