## Output
Output data energy performance
Description | Symbol | Catalogue unit | Computed unit | Validity interval | Intended | Varying | CGN_FUEL | BF | BG | BM | NG | OI
[5 empty] | destination module |  | Egen;in;bf | Egen;in | 0 | 0 | 0 | 0
Generation input | Egen,in,cr | kWh | kWh | 0…∞ | M3-1 | YES | Egen;in;bg | 0 | Egen;in | 0 | 0 | 0
Thermal output | QCHW,gen,out | kWh | kWh | 0…∞ | M10-8 | YES | Egen;in;bm | 0 | 0 | Egen;in | 0 | 0
Electrical output | Eel,gen,out | kWh | kWh | 0…∞ | M3-1 | YES | Egen;in;ng | 0 | 0 | 0 | Egen;in | 0
Recoverable losses | Qgen,ls,rbl,XY | kWh | kWh | 0…∞ | M2-2 | YES | Egen;in;oi | 0 | 0 | 0 | 0 | Egen;in
Auxiliary energy | Wgen,aux | kWh | kWh | 0…∞ | M3-1 | YES | Eel;gen;out | Eel;gen;out | Eel;gen;out | Eel;gen;out | Eel;gen;out | Eel;gen;out
Fuel type | CGN_FUEL |  | - | - | M3-1 | NO

## Input
Product description input data | [7 empty] | Process design input data
Description | Symbol | Unit | Intended |  |  |  |  | Description | Symbol | Unit | Intended
mCHP appliance type | CGN_TYPE | List | [5 empty] | Location of mCHP appliance | CGN_LOC | List
Energy service | CGN_USE | List | M10-8 |  |  |  |  | Hydraulic connection | CGN_HCON | List | M10-8
Fuel type | CGN_FUEL | List | M3-1
Generator number | CGN_NR | - | M10-8
Product technical input data | [7 empty] | Process design input data
Characteristics | Symbol | Catalogue | Computed | Validity interval | Ref. | Varying |  | Description | Symbol | Unit | Intended
|  | unit | Unit |  |  |  |  | mCHP appliance control | CGN_CTR | List
heat output at CHP100%+Sup100% | Pth,chp_100+sup_100 | kW | kW | [0:70] |  | No | 70
power output at CHP100%+Sup100% | Pel,out,chp_100+sup_100 | kW | kW | [0:50] |  | No
auxiliary power CHP100%+Sup100% | Paux,chp_100+sup_100 | kW | kW | [0:20] |  | No
overall efficiency at CHP100%+Sup100% | ɳchp_100+sup_100 | - | - | [0:1.2] |  | No |  | Operating conditions
thermal efficiency at CHP100%+Sup100% | ɳth,chp_100+sup_100 | - | - | [0:1] |  | No |  | Name | Symbol | Unit | Range | Origin | Varying
electrical efficiency at CHP100%+Sup100% | ɳel,chp_100+sup_100 | - | - | [0:0.5] |  | No | [5 empty] | Module
heat output at CHP100%+Sup0% | Pth,chp_100+sup_0 | kW | kW | [0:70] |  | No |  | heat output to the heat distribution sub-system(s) 1) | QCHW,dis,in | kWh | 0...∞ | M3-6 | Yes
nominal power output at CHP100%+Sup0% | Pel,out,chp_100+sup_0 | kW | kW | [0:50] |  | No | [5 empty] | M8-6
auxiliary power at CHP100%+Sup0% | Paux,chp_100+sup_0 | kW | kW | [0:20] |  | No |  | time step | t | h | 1…8760 | M1-9 | Yes
overall efficiency at CHP100%+Sup0% | ɳchp_100+sup_0 | - | - | [0:1.2] |  | No
thermal efficiency at CHP100%+Sup0% | ɳth,chp_100+sup_0 | - | - | [0:1] |  | No
electrical efficiency at CHP100%+Sup0% | ɳel,chp_100+sup_0 | - | - | [0:0.5] |  | No
minimum constant controlled heat output | Pth,min | kW | kW | [0:50] |  | No
standby heat loss | Pls,sb | kW | kW | [0:20] |  | No
power output in standby mode | Pel,out,sb | kW | kW | [0:20] |  | No
auxiliary power in standby mode | Paux,sb | kW | kW | [0:20] |  | No
permanent ignition burner heat input | Ppilot | kW | kW | [0:20] |  | No

## Def_val
Table A.1 - Product description input data |  |  |  |  | Table A.2 - mCHP appliance efficiencies (to be updated)
Description | Symbol | Code | Meaning |  | Characteristics | Symbol | unit | SE | FC | CEG | CED | MT
mCHP appliance type | CGN_TYPE | SE | Stirling engine | 1.05 | overall efficiency | ɳchp_100+sup_100 | - | 0.83 | 0.75 | 0.73 | 0.78 | 0.7
|  | FC | Fuel cell | 0.95 | at CHP_100+Sup_100
|  | CEG | Combustion engine gas | 0.95 | thermal efficiency | ɳth,chp_100+sup_100 | - | 0.61 | 0.35 | 0.45 | 0.5 | 0.52
|  | CED | Combustion engine diesel | 0.95 | at CHP_100+Sup_100
|  | MT | Microturbine | 0.9 | electrical efficiency | ɳel,chp_100+sup_100 | - | 0.1 | 0.25 | 0.21 | 0.3 | 0.13
Energy service | CGN_USE | H | Heating |  | at CHP_100+Sup_100
|  | W | Domestic hot water |  | overall efficiency | ɳchp_100+sup_0 | - | 1.05 | 0.95 | 0.95 | 0.95 | 0.9
|  | C | Cooling |  | at CHP_100+Sup_0
|  | XY | Combination |  | thermal efficiency | ɳth,chp_100+sup_0 | - | 0.95 | 0.7 | 0.61 | 0.6 | 0.66
Fuel type | CGN_FUEL | BF | Biofuel (oil) |  | at CHP_100+Sup_0
|  | BG | Biogas |  | electrical efficiency | ɳel,chp_100+sup_0 | - | 0.25 | 0.5 | 0.38 | 0.4 | 0.32
|  | BM | Biomass (wood) |  | at CHP_100+Sup_0
|  | NG | Natural gas
|  | Ol | Fuel oil
Generator number | CGN_NR | 1-X | M10-8
Table A.3 - Standby heat losses and permanent ignition burner heat input (to be updated)
Characteristics | Symbol | unit | SE | FC | CEG | CED | MT
standby heat loss | Pls,sb | kW | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
permanent ignition burner heat input | Ppilot | kW | 0 | 0 | 0 | 0 | 0
Table A.4 - Process design input data
Description | Symbol | Code | Meaning
Location of mCHP appliance | CGN_LOC | INT | Heated space
|  | UNH | Unheated space
|  | CGN | mCHP appliance room
|  | EXT | External (outdoors)
Hydraulic connection | CGN_HCON | DIR | Direct connection
|  | DEC | Hydraulic decoupling
|  | NCP | condensation prevention pump
|  | HEX | Heat exchanger

## Calc
|  | Measured value | Default value
CGN_TYPE |  |  | 2
CGN_FUEL |  |  | 1
CGN_LOC |  |  | 1
ɳth;chp_100+sup_100 |  | 0.58 | 0.35 | -
ɳel;chp_100+sup_100 |  | 0.143 | 0.25 | -
ɳth;chp_100+sup_0 |  | 0.78 | 0.7 | -
ɳel;chp_100+sup_0 |  | 0.2 | 0.5 | -
Pls;sb |  | 0.7 | 0.7 | kW
Ppilot |  | 0 | 0 | kW
Pth;sb |  |  | 0 | kW
tci |  | 1 |  | h
Pth;chp_100+sup_100 |  | 70 |  | kW
Pel;out;chp_100+sup_100 |  | 10 |  | kW
Paux;chp_100+sup_100 |  | 2 |  | kW
Pth;chp_100+sup_0 |  | 50 |  | kW
Pel;out;chp_100+sup_0 |  | 10 |  | kW
Paux;chp_100+sup_0 |  | 1 |  | kW
QCHW;gen;out |  | 60 |  | kWh |  | M3-6 ; M8-6
Pel;out;sb |  | 0 |  | kW
Paux;sb |  | 0.2 |  | kW
Pth;gen;out = min (Pth;chp_100+sup_100 ; (QCHW;gen;out / t) ) | 1 |  | Pth;gen;out | 60
For Pth;sb < Pth;gen;out < Pth;chp_100+sup_0
Pel;gen;out = Pel;out;sb + (Pel;out;chp_100+sup_0 - Pel;out;sb) * ( (Pth;gen;out - Pth;sb) / (Pth;chp_100+sup_0 - Pth;sb)) | 2
For Pth;chp_100+sup_0 < Pth;gen;out < Pth;chp_100+sup_100
Pel;gen;out = Pel;out;chp_100+sup_0 + (Pel;out;chp_100+sup_100 - Pel;out;chp_100+sup_0) *( (Pth;gen;out - Pth;chp_100+sup_0) / (Pth;chp_100+sup_100 - Pth;chp_100+sup_0)) | 3 |  | Pel;gen;out | 10 | kW
Eel;gen;out = Pel;gen;out * t | 4 |  | Eel;gen;out | 10 | kWh
For Pth;sb < Pth;gen;out < Pth;chp_100+sup_0
Paux = Paux;sb + (Paux;chp_100+sup_0 – Paux;sb) * ((Pth;gen;out - Pth;sb) / (Pth;chp_100+sup_0 - Pth;sb)) | 5
For Pth;chp_100+sup_0 < Pth;gen;out < Pth;chp_100+sup_100
Paux = Paux;chp_100+sup_0 + (Paux;chp_100+sup_100 – Paux;chp_100+sup_0) *( (Pth;gen;out - Pth;chp_100+sup_0) / (Pth;chp_100+sup_100 - Pth;chp_100+sup_0) ) | 6 |  | Paux | 1.5 | kW
Wgen;aux = Paux * t | 7 |  | Wgen;aux | 1.5 | kWh
Pgen;ls;sb = Pls;sb + Ppilot | 8 |  | Pgen;ls;sb | 0.7 | kW
Pgen;in;chp_100+sup_0 = Pth;,chp_100+sup_0 / ɳth;chp_100+sup_0 | 9 |  | Pgen;in;chp_100+sup_0 | 64.1026
Pgen;in;chp_100+sup_100 = Pth;chp_100+sup_100 / ɳth;chp_100+sup_100 | 10 |  | Pgen;in;chp_100+sup_100 | 120.6897
Pgen;ls;chp_100+sup_0 = (1 - ɳth,chp_100+sup_0 - ɳel,chp_100+sup_0 ) * Pgen;in;chp_100+sup_0 | 11 |  | Pgen;ls;chp_100+sup_0 | 1.2821
Pgen;ls;chp_100+sup_100 = (1 - ɳth;chp_100+sup_100 - ɳel;chp_100+sup_100 ) * Pgen;in;chp_100+sup_100 | 12 |  | Pgen;ls;chp_100+sup_100 | 33.431
For Pth;sb < Pth;gen;out < Pth;chp_100+sup_0
Pgen;ls = Pgen;ls;sb+ ( Pgen;ls;chp_100+sup_0 – Pgen;ls;sb ) * ((Pth;gen;out - Pth;sb) / (Pth;chp_100+sup_0 - Pth;sb)) | 13
For Pth;chp_100+sup_0 < Pth;gen;out < Pth;chp_100+sup_100
Pgen;ls = Pgen;ls,chp_100+sup_0 + (Pgen;ls;chp_100+sup_100 – Pgen;ls;chp_100+sup_0 ) * [ (Pth;gen;out - Pth;chp_100+sup_0) / (Pth;chp_100+sup_100 - Pth;chp_100+sup_0) ] | 14 |  | Pgen;ls | 17.3565 |  | 0.77563
Qgen;ls = Pgen;ls * t | 15 |  | Qgen;ls | 17.3565
If CGN_LOC = INT
Qgen;ls;rbl;CHW = Pls;sb * t | 16
If CGN_LOC <> INT
Qgen;ls;rbl;CHW = 0 | 17 |  | Qgen;ls;rbl;CHW | 0.7
Pgen;in = Pth;gen;out + Pel;gen;out + Pgen;ls | 18 |  | Pgen;in | 87.3565
Egen;in = Pgen;in * t | 19 |  | Egen;in | 87.3565
If CGN_FUEL = BF
Egen,in,bf = Egen,in | 20 |  | Egen,in,bf = | 87.3565 | kWh
If CGN_FUEL = BG
Egen,in,bg = Egen,in | 21 |  | Egen,in,bg = | 0 | kWh
If CGN_FUEL = BM
Egen,in,bm = Egen,in | 22 |  | Egen,in,bm = | 0 | kWh
If CGN_FUEL = NG
Egen,in,ng = Egen,in | 23 |  | Egen,in,ng = | 0 | kWh
If CGN_FUEL = OI
Egen,in,oi = Egen,in | 24 |  | Egen,in,oi = | 0 | kWh
ɳel;cgn = (Pel;gen;out) * t / Egen;in | 25 |  | ɳel;cgn | 0.11447
ɳth;cgn = Pth;gen;out * t / Egen;in | 26 |  | ɳth;cgn | 0.68684
tcgn = min (1 ; (QCHW;gen;out /(Pth;chp_100+sup_100 * t))) | 27 |  | tcgn | 0.85714
ɛcgn = Egen;in / (QCHW;gen;out + Eel;gen;out - Wgen;aux) | 28 |  | ɛcgn | 1.2753
Ϭcgn = (Eel;gen;out - Wgen;aux) / Egen;in | 29 |  | Ϭcgn | 0.097302